## Sheet1
ESSENTIAL SPECIFICATIONS FOR REMOTE HYBRID ENERGY SYSTEMS
ITEM | FUNCTION | REQUIRED FUNCTIONALITY OR SPECIFICATIONS
1 | MPPT Charge Controller Autonomous Operation | Each PV Charge Controller must NOT be controlled by the Rectifier System controller, but must operate automously.
2 | MPPT Charge Controller Redundancy | For Redundancy, each MPPT Charge Controller in the system must operate as a stand alone unit to harvest energy from its portion of the PV Array and Charge the Battery independent from all other parts of the system.
3 | Solar Power preference | The control system shall give preference to solar power in case both solar and genset or grid powers are present.
4 | Paralling of Charger Controllers | The unit shall be modular in design with capacity of 4500W. Multiple Solar Chargers may be connected to work in parallel to provide the required load up to 72kW.
5 | Output Current (Modular) | Output Current shall be up to 80 Amps at 48 VDC per Charge Controller and up to 1200 Amps with 16 units in parallel.
6 | Output Power | Output Power shall be up to 4500 Watts at PV Input Voltage between 75V and 179V.
7 | Average energy conversion efficiency | ≥ 98% with load at 25% to 100% and 100VDC input
8 | Warranty | 5 Years
9 | Input voltage window | 75 VDC to 179 VDC
10 | Output Current (Modular) | 80 Amps maximum at 57 VDC
11 | Output Power | ≥ 4500 W
12 | Average energy conversion efficiency | ≥ 98%
13 | Digital display | Backlit LCD display with keypad to check, set and control values and parameters
14 | Battery status display | Controller shall display the condition of battery in % and Amp-hours.
15 | Remote Monitoring capability | The Charge Controller System shall have Remote Interface capabilities.
16 | Data Logging capability | The System with the Remote Monitoring will provide the history analysis going back to the first day of Installation. Monitoring includes PV Voltage and Current, Battery Voltage, Current, Temperature and State of Charge, and the Load Current.
17 | Data Logging Update Rate | New Data shall be uploaded to the System Server for long term storage on the average of once every 1 minute.
18 | Data Logging - Missing Data Update | In the case that the data communicatoin to the Server is interrupted, the system shall retry sending the missing data until the missing data is filled in.
19 | Number of Electronic System Cabinets | The Complete Electronic System shall be in 1 Cabinet for up to 20kW of PV input. Up to 4 Cabinet with up to 16 Charge Controllers total can be wired in parallel.
20 | Cabinet Size | The maximum cabinet size shall be 1200mm Tall x 1000mm Wide x 300mm Deep.
21 | Cabinet Base Footprint | The base of the cabinet is no more than 1000mm Wide x 300mm Deep.
22 | Cabinet access for field service | All components shall be accessable from the front doors of the cabinet.